CONTROLLED POWER COMPANY

MD SERIES - GUIDE SPECIFICATION

3.1 KVA – 7.5 kVA SINGLE PHASE

UNINTERRUPTIBLE POWER SYSTEM

(Optional Items in Red)

1.0	SCOPE

The Uninterruptible Power System (UPS) shall be an expandable single phase, continuous duty, line interactive, single conversion UPS designed to supply reliable, clean regulated power for critical loads.  The design shall incorporate an efficient ferro-resonant transformer, micro-processor controller, solid state PWM inverter and long lasting battery pack that provide immunity to all power line disturbances and power interruptions with no break in AC output power.

The synchronous inverter shall produce a true uninterrupted output in any mode of operation. A self-diagnostic monitoring alarm system that continuously advises system status shall be provided.

2.0	INDUSTRY STANDARDS

The following standards shall apply:

2.1	UL Listed 1778 Standards for UPS.

2.2	C-UL Listed to CSA Standards.

2.3	FCC Class A Limits, 47 C.F.R. Part 15, Subparts A, B.

2.4	IEEE 587 category B guide for surge suppression.

2.5	ANSI/IEEE C62.41 and .45 categories A and B.

2.6	IEC555 Power Factor specifications.

2.7	CBEMA and ANSI C84.1.  Must exceed the specifications and recommendations.

3.0	INPUT SPECIFICATIONS

3.1	INPUT VOLTAGE

(120)(127)(208)(240) VAC, 60 Hz.

(220 VAC, 50 Hz.)

3.2	ELECTRICAL INTERFACE

(Input plug with 8 ft. line cord) (Hardwired input terminals) factory wired to integral thermal magnetic main input circuit breaker.

Engineer’s reference: Consult factory for input plug type and ratings, as well as input circuit breaker ratings. Hardwired input terminals must be selected for 6.0 KVA through 7.5 KVA 120 VAC input models. When specifying a hardwired input, floor mounting channels must be specified in lieu of swiveling lockable casters. Reference section 6.4.

3.3	OPERATING RANGE

+10% to -15% at full load.

  - KVA RATING

(3.0 expandable to 3.5 kVA) (4.5 expandable to 5.0 kVA) (6.0 expandable to 7.5 kVA)

(7.0 expandable to 7.5 kVA) (7.5 kVA)

3.5	FREQUENCY RANGE

Must capture 57.5 Hz to 62.5 Hz (60Hz models).

Must capture 47.5 Hz to 52.5 Hz (50Hz models).

3.6	POWER FACTOR

Must be self correcting to >0.95 (approaching unity).

3.7	INPUT HARMONICS

<5% THD (total harmonic distortion).

3.8	ATTENUATION

Spike attenuation shall be a minimum of 3000:1.

4.0	FUZZY RANGE CONTROL

The UPS shall utilize a Fuzzy Range Control that allows a wider range of input voltage

variation (up to +10% to -40%) of nominal as an inverse function of load.  i.e. As the load

decreases the input band grows wider and more usable while maintaining the output

voltage at usable levels.  Operationally this means the unit must not use battery power

during simple brownout conditions, conserving the batteries for severe power outages.

4.1	FUZZY RANGING

The input range switch points must be infinitely variable as the load decreases.

Input band with 25% load shall be +10% to -40% with an output regulation of +4%.

Input band with 50% load shall be +10% to -30% with an output regulation of +4%.

Input band with 75% load shall be +10% to -20% with an output regulation of +4%.

5.0	OUTPUT SPECIFICATIONS

5.1	OUTPUT VOLTAGE

(120,208)(120/240) VAC, 60 Hz.

(220 VAC, 50 Hz.)

Must provide a Sine Wave Voltage with maximum 3% harmonic distortion for any 	single

harmonic. The output shall be rated for computer type loads with switch mode power

supplies.

5.2	CREST FACTOR

Minimum 3.5 : 1.

5.3	K FACTOR

Must be rated K-30 or better.

5.4	POWER FACTOR

0.7 switch mode rated.

5.5	HARMONIC ATTENUATION

Load generated harmonics shall be attenuated 400% at the input.

5.6	LINE REGULATION

Better than +3%.

5.7	LOAD REGULATION

Better than +3%.

6.0	CABINET

6.1	Cabinet shall be NEMA 1 general purpose indoor type enclosure.

6.2	Cabinet shall be manufactured from at least 16 gauge steel.

6.3	Powder-coat textured paint finish with proper pre-treatment shall be provided.

6.4	Cabinet shall be provided on (swiveling lockable casters) (channels for floor mounting).

Engineer’s reference: Floor mounting channels must be selected for units being specified with a hardwired input / output.

7.0	BATTERY

7.1	Runtime listed at full and half load for each model number with extended run

times available beyond this standard.

(3.1 kVA 8 minutes at full load, 19 minutes at half load.)

(3.5 kVA 7 minutes at full load, 17 minutes at half load.)

(4.5 kVA 9 minutes at full load, 21 minutes at half load.)

(5.0 kVA 7 minutes at full load, 19 minutes at half load.)

(6.0 kVA 11 minutes at full load, 27 minutes at half load.)

(7.0 kVA 8 minutes at full load, 25 minutes at half load.)

(7.5 kVA 7 minutes at full load, 21 minutes at half load.)

Engineer’s reference: Extended runtimes are available, both internal and external to the

UPS. Consult factory for options.

7.2	BATTERY TYPE

Must be sealed, maintenance free, gas recombinant, self venting, suspended

electrolyte with no gel contaminant.  Batteries must be factory tested with specific 		inverter.

7.3 	BATTERY CHARGER

5 amp, two stage, not to exceed 25% of the amp hour rating.

7.4	RECHARGE TIME

3 hours to full charge.

7.5	BUSS VOLTAGE

Float 2.27 VPC, final 1.75 VPC.

7.6	CAPACITY

The batteries shall be sized with the inverter to support the load at rated kVA with

a 0.7 power factor.

7.7	DC CIRCUIT PROTECTION

An integral thermal magnetic DC circuit breaker shall be provided.

8.0	PERFORMANCE

8.1	OVERLOAD CAPABILTY

125% for ten minutes.

8.2	SURGE CAPABILITY

150% of rated output without need of static bypass.

8.3	FREQUENCY STABILITY

+0.2 Hz.

8.4	INNER WINDING CAPACITANCE

.01 pF (primary to secondary coupling).

8.5	COMMON MODE NOISE ATTENUATION

Must be 120 dB or greater (106 : 1 ground noise attenuation).

8.6	TRANSVERSE MODE NOISE ATTENUATION

Must be 70 dB or greater (3160 : 1 line noise attenuation),

(-3 dB at 1 kHz, -20 dB per decade).

8.7	REACTIVE POWER CORRECTION

Load at .6 pF must be corrected to >0.95 at input.

(automatically self-correcting).

8.8	EFFICIENCY & BTU/HR EMITTED

(3.1 kVA minimum efficiency shall be 89% with 814 BTU/HRS emitted.)

(3.5 kVA minimum efficiency shall be 89% with 919 BTU/HRS emitted.)

(4.5 kVA minimum efficiency shall be 89% with 1200 BTU/HRS emitted.)

(5.0 kVA minimum efficiency shall be 89% with 1313 BTU/HRS emitted.)

(6.0 kVA minimum efficiency shall be 89% with 1432 BTU/HRS emitted.)

(7.0 kVA minimum efficiency shall be 89% with 1705 BTU/HRS emitted.)

(7.5 kVA minimum efficiency shall be 89% with 1611 BTU/HRS emitted.)

9.0	DIMENSIONS

(3.1)(3.5)(4.5)(5.0) kVA maximum cabinet dimension shall be 15"W x 29 3/4"D x 22 1/2"H

(6.0)(7.0)(7.5) kVA maximum cabinet dimension shall be 15"W x 29 3/4"D x 30 1/2"H

Engineer’s reference: Cabinet dimensions are for UPS with minimum battery runtimes reflected in section 7.1. Consult factory for cabinet dimensions of UPS with extended battery runtimes.

10.0  	DISPLAY MONITORS AND DIAGNOSTICS

10.1	Digital, 3 digit, bright LED Display shall be provided to display the following

system parameters:

Input Voltage					Percent of Battery Capacity

Output Voltage					Percent of Battery Charger

Percent of Load

10.2	LED indicator lights shall be provided to indicate the following system status:

System On (Green)				System On Battery (Yellow)

Low Battery Warning (Red)

10.3	LED indicator lights shall be provided to indicate the following system Alarms

(Red)

Low output					High output

Overload					Frequency fault

Over temperature				Shorted SCR shutdown

Low battery shutdown				Check battery

Output shutdown				Inverter on

Low battery					Remote/emergency power off shutdown

10.4	AUDIBLE ALARM

A switch selectable audible alarm shall be furnished.

11.0	COMMUNICATIONS INTERFACE

11.1	STATUS AND ALARM PORT

Status / Alarm relay interface normally open contacts shall be provided for remote monitoring and include UPS on, utility AC power failure (system using battery power), low battery warning, system in bypass mode, and general alarm.

11.1	REMOTE EMERGENCY POWER OFF (REPO)

Potential free contact closure REPO input for use with (factory supplied) (customer supplied) REPO push button.

11.2	SERIAL PORT

A full duplex ASCII, RS/232 Serial Port shall be provided to communicate UPS alarms and electrical parameters.

11.3	NETWORK COMMUNICATIONS

The UPS shall include a communications module with integrated webserver for remote monitoring of alarms and electrical parameters via (Ethernet TCP/IP)(MODBUS TCP)(MODBUS RS485).

11.4	AUTOMATIC FILE SERVER SHUTDOWN

The UPS shall be provided with a client-side application software that performs an orderly, unattended shutdown of customer file servers.

12.0	ENVIRONMENTAL

12.1	ISOLATION

Isolation shall be per NEC article 250-5d, and comply with this standard that

specifies a separately derived power source.

12.2	OPERATING TEMPERATURE

Operating Temperature shall be 0°C to 40°C (32°F to 105°F) without derating.

12.3	STORAGE

UPS Storage Temperature (without batteries): -20° to 50°C (-4°F to 122°F).

Battery Storage Temperature: Fully charged batteries at 0°C to 25°C (32°F to 77°F) for 6

months before charging is required. For each 9°C rise, battery reduce storage time by

half.

12.4	HUMIDITY

Relative humidity 95% non condensed.

12.5	ELEVATION

5,000 feet, 1,500 meters.

13.0	MTBF

13.1	SYSTEM

Total System MTBF shall be a minimum of 100,000 hours.

13.2	TRANSFORMER

The Transformer MTBF shall be a minimum or 200,000 hours.

13.3	MTTR

The Mean Time to Repair shall be less than one hour.

14.0	OUTPUT POWER DISTRIBUTION

14.1	The UPS shall be provided with (output terminals for a hardwired installation) (an efficient, flexible method of distributing power from the UPS, without requiring permanent wiring changes).

14.2	Provisions for three output configurations including the appropriately sized branch circuit breakers shall be provided:

14.2.1	FLUSH RECEPTACLE INTERFACE

The back panel must accommodate the specified NEMA standard receptacles.

14.2.2	FLEXIBLE EXTENSION WITH RECEPTACLE TERMINATION

The back panel shall accommodate the specified flexible extension with 		specified receptacle termination.

14.2.3	FIELD WIRED TERMINATION

The following field wired termination shall be furnished:

Engineer’s reference: 3.1kVA through 5.0kVA units are provided standard with (4) NEMA 5-15R1 output receptacles, protected by a single 15 amp fuse. Consult factory for other receptacle options. 6.0 KVA through 7.5 KVA units may be specified with optional output receptacles or a hardwired output termination. Note that all hardwired units must be specified with floor mounting channels in section 6.4.

15.0	BYPASS SWITCH

The UPS shall be provided with following manual bypass switch:

(An internal make-before-break bypass switch that bypasses the UPS electronics, but the output transformer remains in the circuit to provide voltage transformation, regulation, and power conditioning when in the bypass mode.)

(A prewired, 120/240 VAC, 3 wire, wrap-around, make-before-break bypass switch assembly that is attached to the UPS cabinet.)    Engineer’s reference: This bypass option may be used on UPS supplied with an input plug and output receptacles, or a hardwired input / output.

(A prewired, 120/240 or 120/208 VAC, 3 wire, wrap-around, break-before-make bypass switch assembly that is attached to the UPS cabinet.)    Engineer’s reference: This bypass option may be used on UPS supplied with an input plug and output receptacles, or a hardwired input / output.

(A 120/240 VAC, 3 wire, wrap-around, make-before-break maintenance bypass switch provided in a separate wall mountable enclosure, dedicated for a hardwired UPS installation.)

(A 120/240 or 120/208 VAC, 3 wire, wrap-around, break-before-make maintenance bypass switch provided in a separate wall mountable enclosure, dedicated for a hardwired UPS installation.)

16.0	WARRANTY

All systems shall be guaranteed to be free from defects in material and workmanship for a period 1 year following shipment from the factory. Batteries shall be warranted with a 1 year full replacement warranty and an optional 4 year pro-rate with applicable maintenance contract.