Model ES Uninterruptible Power System

60Hz Guide Specification for 4500VA – 15500VA Systems

(Optional Items and Notes in Red)

PART 1 - GENERAL

1.1	DESCRIPTION

This specification defines the electrical and mechanical characteristics and requirements for an on-line, double conversion, uninterruptible power system (UPS), providing immunity from all line disturbances and power interruptions. The system shall incorporate a DSP controlled, high frequency, IGBT PWM rectifier/charger and inverter, an automatic static bypass, intelligent battery charging system, diagnostic monitoring display, secure make-before-break maintenance bypass switch, and all the related hardware components and software to facilitate a functional uninterruptible power system. Batteries shall be provided as specified, prewired and factory tested as a part of the UPS system. The UPS shall include a local monitor to provide complete system diagnostics and continuously advise of system status and battery condition. A high resolution touch-screen display shall be provided for entering user-programmable periodic battery test time and date, set points and viewing system parameters, status, and alarms. The system shall be capable of network communications, remote monitoring and reporting.

- 1.2	STANDARDS

The system shall be designed in accordance with applicable portions of the following standards:

- American National Standards Institute (ANSI C57.110)

- Institute of Electrical and Electronic Engineers (IEEE 519-1992) (C62.41-1991)

- National Electrical Manufacturers Association (NEMA PE-1)

- IEC 62040-3, UPS Performance and Test Requirements

- National Electric Code (NEC 2008)

- National Fire Protection Association (NFPA 70)

- Federal Communications Commission (FCC Part 15, Subpart J, Class A)

- Listed UL Standard – UL 1778 Uninterruptible Power Systems

- C-UL Canadian National Standard C22.2, No. 107.1 M01

  - SUBMITTALS

A.          Manufacturer Requirements:

- The manufacturer shall be ISO 9001:2008 “Quality Assurance Certified” and shall upon request furnish certification documents.

- The manufacturer shall be a United States based manufacturer with 5 years experience or greater in design and fabrication of uninterruptible power systems.

B.          Product Data:

- The manufacturer shall supply documentation for the installation of the system, including wiring diagrams and cabinet outlines showing dimensions, weights, BTUs, input/output current, input/output connection locations and required clearances.

- Factory test results shall be provided to show compliance with the requirements. The manufacturer shall include battery test documentation which demonstrates compliance with the full load battery run time specified.

- The supplier shall furnish (6) equipment submittal copies. Submittals shall be specific for the equipment furnished and shall include as-built information.

PART 2 - PRODUCTS

- 2.1	Manufacturers

The equipment specified shall be the Model ES uninterruptible power system, manufactured by Controlled Power Company.

2.2         Manufactured Units

    - The system shall be designed and manufactured to assure maximum reliability, serviceability and performance. The diagnostic monitor panel display shall be mounted on the front of the system for easy observation of system status and battery condition. The system is to be furnished with an AC input circuit breaker and output distribution as specified. The battery and DC conductors shall be fuse protected. All conductors and transformer windings shall be copper constructed. The input and output conduit locations, input breaker, secure maintenance bypass switch, remote communications interface and output distribution specified shall be located on the rear on the UPS enclosure. The installed UPS shall be designed to meet NEMA 1 standards, rated for indoor use.

    - Normal Operation: The load shall be supplied with regulated power derived from the normal AC input power terminals through the rectifier charger and inverter. The rectifier charger shall be fully rated to charge the batteries and supply sufficient DC energy for the inverter when under full load. The battery shall be connected in parallel with the rectifier charger output.

    - Uninterrupted Emergency Operation: Upon the failure or unacceptable deviation of normal AC input power, energy will be supplied by the battery, through the inverter, and continue to supply uninterrupted power to the load, without switching loss or disturbance. When power is restored at the AC input terminals of the system, the rectifier charger shall continue to supply power to the load, through the inverter, and simultaneously recharge the batteries. There shall be no break or interruption of power to the load upon failure or restoration of the normal AC input power.

    - Automatic Bypass Operation: The system shall include an automatic static bypass for fault clearing, instantaneous overload conditions and/or to connect the load to the normal AC input power source in the event of a system rectifier charger or inverter failure. The automatic static bypass switch shall transfer the load to the normal AC input source with less than a ¼ cycle interruption of power. After the detected fault has cleared, the static bypass switch shall return the load to the UPS output and normal system operation shall resume.

    - Secure Maintenance Bypass / Isolation Switch: The system shall include an integral, wrap around, secure, make-before-break maintenance bypass switch. The switch shall incorporate a push-to-turn function. Pushing the maintenance switch shall invoke the static bypass prior to completing the switch transition to bypass. The maintenance bypass switch shall provide complete isolation of the UPS load terminals from external circuits. When the load is supplied from the normal AC input power source through the maintenance bypass switch, the AC input supply terminals shall remain energized to permit UPS operational checking. A means of disconnecting the AC input source from the rectifier charger and inverter shall exist to allow complete maintenance and replacement of circuit cards or components, without disrupting power to the load. The ability to turn the AC input power source on and off again to the rectifier charger and inverter shall exist to facilitate on-site trouble shooting while the UPS load terminals remain isolated from the load. With the rectifier charger and inverter energized, the UPS system shall be returned to normal mode operation by placing the secure maintenance bypass switch in its normal position via the push to turn function, without disrupting power to the load.

    - System Power Output Capability: The uninterruptible power system’s output power rating shall be (4500) (5500) (6500) (7500) (8300) (9000) (10000) (11000) (12000) (13500) (14500) (15500) VA.

    - Battery Time Reserve Capacity: Battery shall be capable of producing emergency power for (___) minutes at full rated Watts. (Reference Battery Run Time Selection guide at the end of this specification)

    - Batteries: Batteries shall be provided as specified, prewired, and factory tested as a part of the UPS system. Batteries shall be located within the UPS enclosure, without the need for additional cabinetry.

    - System Input Breaker Rating: Input breaker shall be sized to accommodate full rated load, low line input, and maximum recharge current simultaneously.

    - UPS Enclosure: NEMA 1, powder-coat painted steel construction.

    - Cabinet Dimensions: Models with Internal Batteries: (17” x 36.5” x 37.5”) (22.5” x 36.5” x 49”)

VA Rating            Input – Output Voltage	  Dimensions W x D x H  (Battery Time Dependant)

4500 – 5500                     120 – 120 	  (17” x 36.5” x 37.5”) or (22.5” x 36.5” x 49”)

4500 – 11000 	     208/120 – 208/120  	  (17” x 36.5” x 37.5”) or (22.5” x 36.5” x 49”)

4500 – 11000 	     240/120 – 240/120  	  (17” x 36.5” x 37.5”) or (22.5” x 36.5” x 49”)

12000 – 15500 	     208/120 – 208/120  	  22.5” x 36.5” x 49”

12000 – 15500 	     240/120 – 240/120  	  22.5” x 36.5” x 49”

Note: Above input – output voltage configurations do not require an internal isolation transformer.

VA Rating            Input – Output Voltage	  Dimensions W x D x H  (Battery Time Dependant)

4500 – 15500 	     (Other Specified)   	  22.5” x 36.5” x 49”

Note: “Other Specified” input – output voltage configurations require an internal isolation transformer.

    - Internal Isolation Transformer: An internal, computer-grade, shielded isolation transformer shall be provided within the UPS enclosure. External transformer solutions are not acceptable. This transformer shall remain in the circuit while in the maintenance bypass mode, providing the voltage transformation and isolation required.

2.3         Input Specifications

- Input Voltage: (120 VAC) up to 5500 VA, or (208) (208/120) (220) (240) (240/120) (347) (480) (600) VAC.

- Input Voltage Operating Range:  +12% to -15% at full load, without battery usage.

- Extended Range: The unit shall incorporate the use of adaptive input range control in conjunction with the load percentage to extend the input range up to +12% to -50%, without battery usage, while maintaining a regulated output voltage.

- Frequency Range:  57 hertz to 63 hertz.

- Power Factor:  Self correcting to >0.98 (approaching unity).

- Input Current Harmonics:  <5% THD (total harmonic distortion).

2.4         Output Specifications

- Output Voltage: (120 VAC) up to 5500 VA, or (208/120) (240/120) (240/208/120*) VAC.

Note: *Full rated load from a single 120VAC output on models 4500 VA through 11000 VA.

- Sine Wave Voltage:  Maximum 3% THD under linear load. The system shall be capable of supporting non-linear loads with a crest factor of 2.6:1.

- Frequency: 60 hertz + 0.5% under full load while in the battery operation mode.

- Harmonic Attenuation: Reflected load generated harmonics shall be attenuated at the input.

- Voltage Regulation: +/-1.5% from nominal under any load or line conditions within the system ratings.

- Output Power Rating: VA at 0.90 power factor. VA x PF = Watts

- Overload Rating: 200% for 15 cycle, 150% for 30 seconds, 125% for 2 minutes when fed from AC power source.

- On Battery Overload Rating: 125% for 30 cycles, 150% for 3 cycles.

- Efficiency: 87% typical

- Common Mode Noise Attenuation: 70dB minimum with internal shielded isolation transformer.

- Transverse Mode Noise Attenuation: 60dB at 100kHZ with internal shielded isolation transformer.

2.5	Battery Specifications

- Battery time: (___) minutes at full rated watts.

- Battery Type:  Integral, valve regulated, sealed lead calcium, maintenance free.

- Charger:  4 stage, (5 amp) (10 amp), temperature compensated, smart charge. 4 stages shall include the following:

  - Trickle charge to float voltage level in response to a short term discharge.

  - Bulk charge providing maximum recharge power following a deep discharge.

  - Temporary equalize charge as required.

  - Maintained float charge to assure full battery capacity.

Note: 5 amp charger used with battery options A and B; 10 amp charger used with battery options C through J.

- Recharge Time:  <10 times the discharge period to 90% capacity.

- Bus Voltage:  120 VDC.

- Battery Rating: Battery case shall have a UL 94-V2 minimum rating for installation within a computer room.

2.6         Environmental Specifications

- Operating Temperature:  System shall be designed and UL listed for operation at 0°C to 40°C. Optimum battery performance and life shall be achieved at 25°C.

- UPS Storage Temperature:  -20°C to 50°C.

- Battery Storage Temperature:  25°C for 6 months. For each 9°C rise, reduce storage time by half.

- Relative Humidity:  95% non-condensing.

- Elevation:  5,000 feet (1,500 meters).

- Audible Noise Level: 52 to 54 dba at 3 feet, size and model dependant.

2.7	 Display Monitor and Diagnostics

    - Display Panel: The system shall include a local monitor to provide complete system diagnostics and continuously advise of system status and battery condition. A high resolution LCD touch-screen display shall be provided for entering user-programmable periodic battery test time and date, set points and viewing system parameters, status, and alarms.

- The monitor shall display the following electrical parameters:

Input Voltage
Output Voltage L1-N

Output Voltage L2-N

Output Current L1-N

Output Current L2-N

Output Volt-Amperes L1-N

Output Volt-Amperes L2-N

Output Volt-Amperes Total

Output Watts L1-N

Output Watts L2-N

Output Watts Total

Output Power Factor L1 – N

Output Power Factor L2 – N

Output Power Factor Total

Output Percent Load L1-N

Output Percent Load L2-N

Output Percent Load Total

Output Frequency

Battery Voltage	
Battery Charger Current

- The monitor shall display the following status and alarm conditions:

Input Voltage High/Low

Output Voltage L1-N High/Low

Output Voltage L2-N High/Low

Output Volt-Amperes High - Overload

Output Frequency High/Low

Battery Voltage High/Low

Battery Charger Current High

General Alarm

System On Battery

Low Battery Warning

Low Battery Shutdown

UPS Over-temperature Warning

DC Charger Failure / DC Open

REPO Shutdown

System in Manual Bypass

System in Static Bypass

Battery Test Pass

Battery Test Fail

- The monitor shall display the following operational conditions:

System Normal

Percent Battery Time Remaining

Battery Test In Process

- User Programmable Interface: Programming of high/low alarm threshold settings and automatic periodic battery testing shall be via the local monitor’s touch-screen display, without the need for an external computer and cable.

- Manual Test: The monitor shall feature a manual, proprietary, password protected “Push to Test” feature to initiate a 30 second battery test.

- Automatic Test: The monitor shall feature a user programmable automatic 30 second battery test. The user shall be able to set the time, date, and frequency of the battery test.

- Automatic Test Results: The monitor shall report the results of the automatic battery test with a pass/fail indication, time and date stamped via the local monitor’s touch-screen display.

- Automatic Test Log: The monitor shall maintain a historic log that sequentially records 25 battery tests which indicate time, date and pass/fail results. The log shall be made available through the LCD touch-screen display of the monitor.

- Status Alarm Log: The monitor shall maintain a historic log that sequentially records 25 status alarms which indicate time and date of abnormal occurrences. The log shall be made available through the LCD touch-screen display of the monitor.

2.7	Remote Communications Capability

    - Serial Communications: A standard USB port shall be provided for authorized access to electrical parameters, system status, alarms, system set point programming, and the test and alarm logs.

    - Network Communications: Optional slot cards shall be available for remote monitoring and reporting of electrical parameters, system status, alarms, event logs, and automatic battery test results. Network communication options shall include Ethernet TCP/IP, MODBUS TCP, or MODBUS RS485.

    - Relay Contacts: A standard hardwired terminal strip interface shall be provided for remote indication of UPS on battery, low battery warning, on static bypass, and general alarm. Relay contacts shall be potential free, normally open, and rated for 120VAC @ .5 amps.

    - Emergency Shutdown: A hardwire terminal connection shall be provided for customer’s remote emergency power off (REPO), normally open input contact.

2.8	Output Distribution Capability

Output distribution options shall be available and include hardwired output terminals, up to (4) (6) locking receptacles and (3) (4) non-locking duplex receptacles. For hardwired installations, up to (8) (16) output circuit breaker pole spaces shall be available. (Reference Output Distribution Selection guide at the end of this specification)

2.9	Optional Equipment Specified

    - No options specified.

    - Include one (1) slot card for remote monitoring and reporting of electrical parameters, system status, alarms, event logs, and automatic battery test results via (Ethernet TCP/IP) (MODBUS TCP) (MODBUS RS485).

    - Include a quantity of (_) locking receptacles, type (L5-20R) (L5-30R) (L6-20R) (L6-30R) (L14-20R) (L14-30R), each with their own circuit breaker, and a quantity of (_) locking receptacles, type (_______).

    - Include a quantity of (_) non-locking duplex receptacles, type (5-15R2) (5-20R2), each with their own circuit breaker.

    - Include a quantity of (__) output breakers, 1 pole, (15) (20) (30) (40) (50) amp, 120 VAC, and a quantity of (__) output breakers, 1 pole, (15) (20) (30) (40) (50) amp, 120 VAC, for customer’s hardwired connection.

    - Include a quantity of (__) output breakers, 2 pole, (20) (30) (40) (50) (60) (70) (80) (90) (100) amp, (208) (240) VAC, and a quantity of (__) output breakers, 2 pole, (20) (30) (40) (50) (60) (70) (80) (90) (100) amp, (208) (240) VAC, for customer’s hardwired connection. (See Engineering Reference page 8 for breaker selection criteria.)

    - Include an automatic message dialer for telephone messaging to inform maintenance personnel of system alarm conditions for UPS on battery power, low battery warning, on static bypass, and general alarm.

    - Include a remote annunciator panel, with an audible alarm and alarm silence, for remote status indication of system alarm conditions including UPS on battery power, low battery warning, on static bypass, and general alarm.

2.10	Warranty

    - The manufacturer shall guarantee the UPS electronics and controls to be free from defects in material and workmanship for a period of (3) years following shipment from the factory.  The battery warranty shall be 2-year full replacement, and an optional 3-year pro-rate with applicable maintenance contract.  On site labor for warranty repair in the United States and Canada shall be covered for 90 days following shipment from the factory.

End of Specification

ENGINEER’S REFERENCE

Battery Run Time / Enclosure Selection

| Output Power |  | UPS Cabinet Style S w/ Internal Battery |  | UPS Cabinet Style T w/ Internal Battery |  |  |  |  | UPS Cabinet Style T w/ One External Battery Cabinet |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VA | Watt | A | B | A | B | C | D | E | F | G | J |  |  |
| 4500 | 4050 | 7 | 25 | 7 | 25 | 35 | 40 | 70 | 100 | 180 | 290 |  |  |
| 5500 | 4950 | 5 | 17 | 5 | 17 | 27 | 30 | 50 | 75 | 120 | 225 |  |  |
| 6500 | 5850 |  | 14 |  | 14 | 19 | 25 | 48 | 60 | 105 | 170 |  |  |
| 7500 | 6750 |  | 12 |  | 12 | 17 | 18 | 38 | 48 | 90 | 150 |  |  |
| 8300 | 7470 |  | 9 |  | 9 | 15 | 17 | 36 | 45 | 79 | 120 |  |  |
| 9000 | 8100 |  | 7 |  | 7 | 12 | 14 | 28 | 40 | 70 | 110 |  |  |
| 10000 | 9000 |  | 6 |  | 6 | 11 | 12 | 24 | 35 | 60 | 105 |  |  |
| 11000 | 9900 |  | 4 |  |  | 8 | 11 | 18 | 30 | 55 | 90 |  |  |
| 12000 | 10800 |  |  |  |  | 7 | 10 | 17 | 27 | 45 | 80 |  |  |
| 13500 | 12150 |  |  |  |  | 6 | 7 | 14 | 25 | 40 | 70 |  |  |
| 14500 | 13050 |  |  |  |  |  | 5 | 13 | 18 | 30 | 65 |  |  |
| 15500 | 13950 |  |  |  |  |  |  | 12 | 17 | 27 | 60 |  |  |
| Battery Weights (See battery option letter; indicator in the above matrix) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A = 218 lbs B = 277 lbs C = 318 lbs D = 451 lbs E = 616 lbs F = 1297 lbs G = 1627 lbs J = 2238 lbs |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Notes: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Add the selected battery option weight above to the UPS unit weight (w/o batteries) to arrive at the total system weight. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Battery options F through J require an external battery cabinet, together with UPS cabinet style T. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The external battery cabinet matches the dimensions of the UPS cabinet style T (22.5"W x 36.5"D x 49"H). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Optional batteries available with a UL 94-V2 minimum battery case rating, for installation within a computer room. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| * Longer battery run times are available other than those listed above. Consult factory for details. |  |  |  |  |  |  |  |  |  |  |  |  |  |

ENGINEER’S REFERENCE

Output Distribution Selection

| Available on UPS Cabinet S |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Breaker with Receptacle: Maximum of 3, Non-Locking Receptacles |  |  |  |  |  |  |
|  | Maximum of 4, Locking Receptacles |  |  |  |  |  |
| Breaker Only Option for Hardwire Connection: Maximum of 8 Poles up to 30A |  |  |  |  |  |  |
|  |  | Maximum of 6 Poles up to 60A |  |  |  |  |
| Available on UPS Cabinet T |  |  |  |  |  |  |
| Breaker with Receptacle: Maximum of 4, Non-Locking Receptacles |  |  |  |  |  |  |
|  | Maximum of 6, Locking Receptacles |  |  |  |  |  |
| Breaker Only Option for Hardwire Connection: Maximum of 16 Poles up to 30A |  |  |  |  |  |  |
|  |  | Maximum of 14 Poles up to 60A Maximum of 12 Poles up to 100A |  |  |  |  |

Available Breaker Only Options for Hardwire Connection

| Breaker / Pole | Voltage | Phase |
| --- | --- | --- |
| 15A / 1P | 120V | 1 |
| 20A / 1P | 120V | 1 |
| 30A / 1P | 120V | 1 |
| 40A / 1P | 120V | 1 |
| 50A / 1P | 120V | 1 |
| 20A / 2P | 208V | 2 |
| 20A / 2P | 240V | 2 |
| 30A / 2P | 208V | 2 |
| 30A / 2P | 240V | 2 |
| 40A / 2P | 208V | 2 |
| 40A / 2P | 240V | 2 |
| 50A / 2P | 208V | 2 |
| 50A / 2P | 240V | 2 |
| 60A / 2P | 208V | 2 |
| 60A / 2P | 240V | 2 |

Main Output Breakers larger than 60A available on UPS Cabinet T Only

| 70A / 2P | 208V | 2 |
| --- | --- | --- |
| 70A / 2P | 240V | 2 |
| 80A / 2P | 208V | 2 |
| 80A / 2P | 240V | 2 |
| 90A / 2P | 208V | 2 |
| 90A / 2P | 240V | 2 |
| 100A / 2P | 208V | 2 |
| 100A / 2P | 240V | 2 |