Model ESV Uninterruptible Power System

Guide Specification for 1.5 KVA/KW – 14.0 KVA/KW Systems

- (Optional Items In Red)

- Part 1

  - General

This specification defines the electrical and mechanical characteristics and requirements for an on-line, dual conversion, uninterruptible power supply (UPS) system. The system as specified herein includes all the components required to deliver reliable, high quality uninterruptible power for mission critical equipment. The system shall incorporate a microprocessor-based, DSP controlled, input power factor corrected, high-frequency IGBT PWM rectifier/charger, together with an IGBT PWM inverter and high speed fail-safe SCR automatic bypass transfer circuit. These components and battery backup shall function to provide immunity from all line disturbances and power interruptions, with no loss or break in AC output power. The specified UPS system shall have a front access enclosure design to provide extended battery runtime, facilitate centralized UPS installation, and accommodate vertical overhead cable landings. A an advanced, full diagnostic, monitoring and testing system with color touch screen LCD display panel and network remote communications shall continuously advise of system status and battery condition. The UPS system shall include a manual bypass switch for maintenance and periodic battery replacement.

  - Standards

The systems shall be designed in accordance with applicable portions of the following standards:

    - American National Standards Institute (ANSI C57.110).

    - Institute of Electrical and Electronic Engineers (IEEE 519-2014) (C62.41-2002).

    - National Electrical Manufacturers Association (NEMA PE-1).

    - National Electric Code (NEC 2005, Article 700).

    - Underwriters Laboratories (UL) (C-UL to CSA Standards).

    - Federal Communications Commission (FCC Part 15, Sec. J, Class A).

    - Federal Aviation Administration (FAA-G-201e).

    - Listed UL Standards UL 1778 UPS Equipment and C-UL listing to CSA C22.2, No. 107.1-M01 Canadian Standards for UPS Equipment.

  - Submittals

    - The manufacturer shall supply documentation for the installation of the system, including wiring diagrams and cabinet outlines showing dimensions, weights, BTUs, input/output current, input/output connection locations and required clearances.

    - The manufacturer shall be ISO9001 “Quality Assurance Certified” and shall upon request furnish certification documents.

    - The manufacturer shall be a United States based manufacturer with 5 years experience or greater in design and fabrication of uninterruptible power systems.

    - Factory test results shall be provided to show compliance with the requirements. The manufacturer shall include battery test documentation to validate the specified minimum emergency reserve with full rated KVA/KW load.

    - The supplier shall furnish (6) equipment submittal copies. Submittals shall be specific for the equipment furnished and shall include as-built information.

Part 2

- 2.1	Manufacturers

The equipment specified shall be the Model ESV uninterruptible power system, manufactured by Controlled Power Company.

2.2        Manufactured Units

The system shall be designed and manufactured to assure maximum reliability, serviceability and performance. The system shall include one main control module for rapid service or replacement. The local display shall be mounted on the front of the system for easy observation of system status and battery condition. The system is to be furnished with an internally located AC input circuit breaker and output distribution panel. The battery and DC conductors shall be DC fuse protected. All conductors and transformer windings shall be copper constructed. Cabinets are floor mountable, constructed of steel, front accessible through a hinged, key lockable door and shall be NEMA 1 rated for indoor use.

    - Normal Operation: The load shall be supplied with regulated power derived from the normal AC power input terminals through the rectifier charger and inverter. The rectifier charger shall be fully rated to charge the batteries and supply sufficient DC energy for the inverter when under full load. The battery shall be connected in parallel with the rectifier charger output.

    - Uninterrupted Emergency Operation: Upon the failure or unacceptable deviation of commercial AC power, energy shall be supplied by the battery through the inverter and continue to supply power to the load without switching loss or disturbance. When power is restored at the AC input terminals of the system, the rectifier charger shall continue to supply power to the load through the inverter and simultaneously recharge the batteries. There shall be no break or interruption of power to the load upon failure or restoration of the commercial AC power.

    - Automatic Bypass Operation: The system shall include an automatic bypass switch for fault clearing, instantaneous overload conditions and/or to connect the load to the normal utility source in the event of a system rectifier charger or inverter failure.

    - Secure Internal Maintenance Bypass / Isolation Switch: The system shall include an integral, make-before-break maintenance bypass switch accessible via the front of the UPS enclosure through a hinged, key lockable door. The switch shall incorporate a push-to-turn function. Pushing the maintenance switch shall invoke the static bypass prior to completing the switch transition to bypass. When in the bypass position, the maintenance bypass switch shall provide complete isolation of the UPS output from external circuits. When the load is supplied from the normal AC input power source through the maintenance bypass switch, the AC input supply terminals shall remain energized to permit UPS operational checking. A maintenance circuit breaker shall be provided as means of disconnecting the AC input source from the rectifier charger and inverter, and shall allow complete maintenance and replacement of circuit cards or components without disrupting power to the load. The maintenance circuit breaker shall provide the ability to turn the AC input power source off and on again to the rectifier charger and inverter to facilitate on-site trouble shooting while the UPS output remains isolated from the load. With the rectifier charger and inverter energized, the UPS system shall be returned to normal mode operation by placing the secure maintenance bypass switch in its normal position via the push to turn function, without disrupting power to the load. This internal method of bypass shall maintain the UPS’s input – output voltage configuration.

    - Break-Before-Make External Maintenance Bypass: On UPS systems where the nominal input and output voltages are the same and output distribution breakers are external from the UPS enclosure, an external, wall mounted, push to turn, break before make, wrap around maintenance bypass switch shall be provided for field installation. When in bypass mode, the switch shall bypass the UPS system and feed the load power directly from the AC input power source. The UPS system’s main input breaker shall then be opened, allowing the UPS to be fully serviced, including the complete maintenance and replacement of circuit cards or components. The bypass switch shall include an auxiliary contact to indicate the position of the switch (normal or bypass) for remote monitoring purposes. The bypass switch shall be provided with a padlock attachment for lockout purposes during maintenance.

    - Make-Before-Break External Maintenance Bypass: On UPS systems where the nominal input and output voltages are the same and output distribution breakers are external from the UPS eclosure, an external, wall mounted, push to turn, make before break, wrap around maintenance bypass switch shall be provided for field installation. When in bypass mode, the switch shall bypass the UPS system and feed the load power directly from the AC input power source. The UPS system’s main input breaker shall then be opened, allowing the UPS to be fully serviced, including the complete maintenance and replacement of circuit cards or components. The bypass switch shall include an auxiliary contact to indicate the position of the switch (normal or bypass) for remote monitoring purposes. A second auxiliary contact shall be wired to the UPS and shall invoke the system’s static bypass before the switch is turned to the bypass position. The bypass switch shall be provided with a padlock attachment for lockout purposes during maintenance.

    - System Power Output Capability: The stored emergency power supply system output power rating shall be    (1.5 KVA/KW)  (2.2 KVA/KW)  (3.0 KVA/KW)  (3.5 KVA/KW)  (4.2 KVA/KW)  (5.0 KVA/KW)             (6.0 KVA/KW)  (7.0 KVA/KW)  (7.5 KVA/KW)  (8.5 KVA/KW)  (10.0 KVA/KW)  (12.5 KVA/KW)      (13.5 KVA/KW)  (14.0 KVA/KW).

    - Battery Time Reserve Capacity: Battery shall be capable of producing emergency power for (__) minutes at full rated watts.

    - Reliability: MTBF 100,000 hours. MTTR, 1 Hour.

Part 3

3.1	Input Specifications

3.1.1	Input Voltage:

(120) (277) VAC  (on models 1.5 KVA and 2.2 KVA)

(120) (208/120) (240/120) (277) VAC  (on models 3.0 KVA and 3.5 KVA)

(120) (208/120) (220) (240/120) (277) (347) (480) (600) VAC  (on models 4.2 KVA and 5.0 KVA)

(208/120) (220) (240/120) (277) (347) (480) (600) VAC  (on models 6.0 KVA through 14.0 KVA)

3.1.2		Input Voltage Operating Range:  +12% to -15% at full load without battery usage.

3.1.3		Extended Range: The unit shall incorporate the use of variable range logic in conjunction with the load percentage to extend the input range up to +12% to -30% without battery usage while maintaining a regulated, usable output voltage.

3.1.4	Frequency Range:  57.5 Hz to 62.5 Hz.

3.1.5	Power Factor:  Self correcting to >0.97 (approaching unity).

3.1.6	Input Current Harmonics:  <5% THD (total harmonic distortion).

3.2	Output Specifications

- 3.2.1	Output Voltage:

(120) VAC  (on models 1.5 KVA and 2.2 KVA)

(120) (208/120) (240/120) VAC  (on models 3.0 KVA and 3.5 KVA)

(120) (208/120) (220/127) (240/120) VAC  (on models 4.2 KVA through 14.0 KVA)

- 3.2.2   	Sine Wave Voltage:  Maximum 3% harmonic distortion under linear load.

- 3.2.3	Frequency: 60 hertz + 0.5% under full load while in the battery operation mode.

3.2.4	Harmonic Attenuation: Reflected load generated harmonics shall be attenuated at the input.

    - Voltage Regulation: +/-2%.

    - Output Power Rating: KVA at 1.0 power factor (unity). KVA = KW

3.3	Battery Specifications

3.3.1	Battery time: (__) Minutes at full rated kilowatt output capability, UL 1778 Listed.

3.3.2	Battery Type:  Integral, valve regulated, sealed lead calcium, maintenance free.

3.3.3	Charger:  4 stage, temperature compensated, (700) (1400) watts, 1% ripple filtered.

Engineer’s note: 700 watts on models 1.5 KVA/KW through 5.0 KVA/KW.

1400 watts on models 6.0 KVA/KW through 14.0 KVA/KW.

3.3.4	Bus Voltage:  120 VDC.

3.3.5	Installation:  Batteries shall be shipped loose for field installation by the electrical contractor.

3.4	Performance Specifications

    - Overload Rating:

(105% continuous, 125% for 10 seconds, and 1000% for 3 cycles when fed from AC power source).            Engineer’s note: On models 1.5 KVA/KW through 3.5 KVA/KW.

(125% for 2 minutes, 150% for 30 seconds and 200% for 15 cycles when fed from AC power source).    Engineer’s note: On models 4.2 KVA/KW through 14.0 KVA/KW.

    - On Battery Overload Rating: 125% for 30 cycles, 150% for 3 cycles.

    - Voltage Regulation: The output voltage shall be regulated to within +2% during input voltage changes from +12% to – 15% with reference to nominal, and when the output is loaded from no load to full rated load.

    - Common Mode (isolation transformer units only):  120 dB (106 : 1 ground noise attenuation).

    - Transverse Mode (isolation transformer units only):  70 dB (3160 : 1 line noise attenuation).

Engineer’s note: Consult factory for models available with an internal isolation transformer.

    - Reactive Power Correction:  Load at .6 pf corrected to > 0.97 at input (automatically correcting).

    - Efficiency: 86% typical under full rated load.

    - Reliability: 100,000 hours MTBF.

3.5	Environmental Specifications

3.5.1	Operating Temperature:  0°C (32°F) to 40°C (104°F).

- 3.5.2	Storage Temperature:  -20°C to 50°C

3.5.3	Relative Humidity:  95% non-condensing.

3.5.4	Elevation:  5,000 feet, 1,500 meters without de-rating.

    - Audible Noise Level: Not greater than 50 dba at 1 meter.

3.6	Enclosure Specifications

3.6.1	Description: Shall be a floor-mounted, NEMA 1 vertical front access cabinet with top-side conductor cable

landings to facilitate centralized installation for server racks and/or other critical equipment.

- 3.6.2	Construction:  The top and all sides of the enclosure shall be constructed from 14 gauge steel, and the base

- constructed from 12 gauge steel. The enclosure steel shall be pre-treated and finished with a powder-coat

- paint to resist corrosion, marring or scratching.

3.6.3	Access: A hinged, key lockable front door shall be provided for access to all components and batteries. Side

and back access shall not be required for system installation, operation, or service.

3.6.4	Breakers Location: A hinged, key lockable breaker panel door shall be provided for access to input and

output circuit breaker.

Part 4

4.1	 Display Monitor and Diagnostics

    - Display Monitor –  A display monitor shall be included. The UPS system shall include a local, front mounted, sealed, touch screen, LCD display monitor to verify system electrical and temperature measurements, inform/alarm for abnormal system status, allow programming of user specified set points and inform of periodic system and battery test results.

4.1.1.1	The monitor shall display the following electrical parameters:

Input Voltage
			Output Voltage

Output Current

Output Volt-Amperes

Output Watts

Output Power Factor

Output Percent Load

Output Frequency

Battery Voltage	
			Battery Charger Current

4.1.1.2	The monitor shall display the following status and alarm conditions:

Input Voltage High/Low

Output Voltage High/Low

Output Volt-Amperes High - Overload

Output Volt-Amperes Low

Output Frequency High/Low

Battery Voltage High/Low

Battery Charger Current High

General Alarm

System On Battery

Low Battery Warning

Low Battery Shutdown

Inverter Over-temperature Warning

DC Charger Failure / DC Open

Output Circuit Breaker Open

REPO Shutdown

System in Manual Bypass

System in Static Bypass

Battery Test Pass

Battery Test Fail

4.1.1.3	The monitor shall display the following operational conditions:

System Normal

Percent Battery Time Remaining

Battery Test In Process

    - Programming User Specified Set Points – Include provisions for user interface programming of system status  for high/low alarm threshold set points, and the frequency of the automatic battery test.

    - The monitor shall feature a manual, proprietary, password protected “Push to Test” feature.

    - Periodic Testing - The monitor shall feature diagnostics for automatic and manual battery testing.

      - It shall feature a 30 second battery discharge test every 7 days, 30 days or 90 days.

      - It shall report the results of the battery test with a pass/fail indication, time and date stamped via the local monitor panel and/or via (E-mail, SNMP, Ethernet TCP/IP or MODBUS TCP or BACnet/IP ) (MODBUS RTU or ASCII over RS485, or BACnet MS/TP). (An optional Multifunction Communications Modem shall be provided so test results can be sent via fax, voice messaging and/or web page generation.)

    - Periodic Testing Log - The monitor shall maintain a historic log that sequentially records 25 battery tests which indicate time, date and pass/fail results. The log shall be made available through the LCD display of the monitor and remote communication capabilities.

    - Status Alarm Log - The monitor shall maintain a historic log that sequentially records 25 status alarms which indicate time and date of abnormal occurrences. The log shall be made available through the LCD display of the monitor and remote communication capabilities.

4.2	Communications

4.2.1	The monitoring system shall contain a  9 pin status / alarm port with potential free 24VAC and/or DC 500mA rated contacts and a terminal strip with potential  free, 120V 500mA rated contacts for use with an optional remotely located audible / visual annunciator panel, optional automatic message dialer, optional fax modem, or optional computer network integration adapter.

    - Alarm Port - Include provisions to remotely communicate and/or notify of system on battery power, low battery, general alarm and system on bypass.

    - Alarm Relay Contacts - Include hardwire terminal strip connections to alarm relay contacts that remotely communicate and/or notify of UPS on battery power, low battery, general alarm, system on bypass, battery test pass and battery test fail occurrences.

    - Battery Test Active Contact - A normally closed battery test active contact shall be provided that opens during automatic or manual system testing.

    - Computer Port - The system shall include provisions to communicate UPS status and alarm conditions to a single computer or across a computer network via optional network communication.

Part 5

5.1	Accessories (Optional Equipment)

    - Include automatic message dialer for telephone messaging to inform maintenance personnel of system alarm conditions for system on emergency battery power, low battery warning, or general alarm.

    - Include remote annunciator panel for remote status indication of system alarm conditions for system on emergency battery power, low battery warning, general alarm, and battery test active. The annunciator panel shall be provided with an interface cable of (50) (100) (150) (200) feet to connect to the UPS communication port.

    - Include (SNMP / Ethernet TCP/IP / MODBUS TCP / BACnet/IP) (MODBUS RTU or ASCII over RS485 / BACnet MS/TP) for network communication of UPS status and electrical measurement data.

    - Include (quantity) pre-installed, 20 amp output circuit breakers. (Max. 20 pole positions).

    - Include an output circuit breaker open or tripped alarm contact on all output circuit breakers for use with remote and/or local annunciation indicators. (Each alarm contact added requires ½ pole position for single pole breakers, and 1 pole position for two pole breakers. Max 20 pole positions available.).

Part 6

6.1	Warranty

    - The manufacturer shall guarantee all power component and system electronics to be free from defects in material and workmanship for a period of 2 years following shipment from the factory.

    - Battery warranty shall be 2-year full replacement, and an optional 3-year pro-rate with applicable maintenance contract.   On site labor for warranty repair in the United States and Canada shall be covered for 90 days following shipment from the factory.

6.2	Serviceability

Each UPS contains one front-accessible electronics module subassembly. Batteries shall be positioned and wired to facilitate rapid replacement.