CONTROLLED POWER COMPANY

GUIDE SPECIFICATION

FOR THE POWER COMMANDER PLUS

SERIES 900/200 ELECTRONIC LINE VOLTAGE REGULATOR

1.0	General

This specification describes the electrical and physical aspects of an electronic line voltage regulator (EVR) with an internal computer grade isolation transformer. All systems shall be designed and manufactured to assure maximum reliability, flexibility, serviceability and performance. The EVR shall use seamless electronic control to provide output voltage regulation within 1% of nominal. The output shall be adjustable ± 10% from nominal with an internal potentiometer. In addition to tight voltage regulation, the EVR shall step the voltage up or down to the desired level, give isolation, and provide transient and noise attenuation.

The system shall be Controlled Power Company’s Power Commander Series 900/200 or Owner / Engineer approved Equal.

2.0	Standards

The EVR shall be designed and manufactured in accordance with the following standards:

- Institute of Electrical and Electronic Engineers (IEEE 597) 
- National Fire Protection Association (NFPA 70), National Electrical Code (NEC)
- Underwriters Laboratory (UL 1012)

3.0	Performance Specifications

3.1	System Rating:  The system shall be rated at ______________ KVA.

3.2	Input Voltage - Nominal A.C. input voltage shall be ____________ Volts, _____ Phase.

3.3	Output Voltage - Nominal A.C. output voltage shall be ____________Volts, _____ Phase.

3.4	Output Voltage Regulation - Shall be + 1% or better for input voltage fluctuations of +10%

to -20% of nominal, and from no load to full load.

3.5	Remote Sensing - The output voltage shall be able to be sensed and regulated at the load, automatically compensating for line and wire losses due to long distances to the load.

3.6	Frequency Range - Shall be 57 to 63 Hz for 60 Hertz models, or 48 to 52 Hz for 50 Hertz models.

3.7	Output Voltage Adjustment Range - Shall be adjustable to + 10% with internally located potentiometer.

3.8	Correction Time - Shall be 5 to 9 cycles under worst case conditions.

3.9	Efficiency - Shall be 89% to 92%, KVA size dependent.

3.10	Power Factor - Shall be 0.95 typical at full load.

3.11	Harmonic Content - Less than 5% THD shall be added under linear load.

3.12	Overload Capability - Shall be 500% for 10 seconds, 1000% for one cycle. Shall conform to IEEE 597.

3.13	Audible Noise – Shall be less than 60dBA @ 1 meter.

3.14	MTBF shall be a minimum of 100,000 hours.

4.0	Regulating Transformer

4.1	Transformers shall be buck-boost dry type, convection or fan air cooled, 600 volt class.

4.2	The transformer shall be electrically and magnetically regulated with no moving parts.

4.3	All transformer windings shall be class N (200 C) insulated copper.

4.4	A class N installation system shall be utilized throughout with operating temperatures not to exceed 115C over a 40C ambient temperature.

4.5	Transformer core manufactured shall utilize M-6 grade, grain oriented, stress relieved silicon transformer steel.

4.6	Interface terminals shall be provided for input and output conductors.

4.7	All leads, wires and terminals shall be labeled to correspond with circuit wiring diagram.

4.8	Transformers shall be vacuum impregnated with an epoxy resin.

5.0	Input Isolation Transformer   (Three Phase units only)

5.1	The isolation transformer shall be configured in a three phase delta primary and include

taps at 2.5% increments, with two (2) above and four (4) below the nominal voltage.

5.2	Input terminals shall be provided for input conductors.

5.3	The transformer secondary shall be "wye" configured with three phase conductors and a

newly derived neutral conductor. The newly derived neutral shall be effectively bonded to

the cabinet enclosure and a grounding terminal lug, so the isolated output will be

effectively referenced (grounded).

5.4	Common Mode noise attenuation shall be 120dB or better.

5.5	The transformer windings shall be all copper conductor construction, with separate

primary and secondary isolated windings. The transformer shall conform to NEC article

250-5D, that specifies a separately derived power source.

5.6	The transformer shall incorporate a solid foil, double copper electrostatic shield to

minimize inner winding capacitance, as well as transient and noise coupling between

primary and secondary windings.

5.7	Grain oriented, M6 grade, silicon transformer steel shall be utilized.

5.8	Flux density shall not exceed 15K gauss.

5.9	Class N, 200°C insulation systems shall be used throughout with a maximum temperature

rise of 115°C above an ambient of 40°C.

5.10	The transformer shall be designed for natural convection cooling.

5.11	Transverse Mode noise attenuation shall be 3 dB at 1000 hertz and 20 dB per decade to

50 dB with a resistive load.

6.0	Output Isolation Transformer   (Single Phase units only)

6.1	The isolation transformer shall include primary taps at 2.5% increments, with two (2) above

and four (4) below the nominal voltage.

6.2	The newly derived neutral shall be effectively bonded to the cabinet enclosure and a

grounding terminal lug, so the isolated output will be effectively referenced (grounded).

6.3	Output terminal lugs shall be provided for termination of the output phase conductors, one

neutral conductor, and one ground conductor.

6.4	Common Mode noise attenuation shall be 120dB or better.

6.5	The transformer windings shall be are all copper conductor construction, with separate

primary and secondary isolated windings. The transformer shall conform to NEC article

250-5D, that specifies a separately derived power source.

6.6	The transformer shall incorporate a solid foil, double copper electrostatic shield to

minimize inner winding capacitance, as well as transient and noise coupling between

primary and secondary windings.

6.7	Grain oriented, M6 grade, silicon transformer steel shall be utilized.

6.8	Flux density shall not exceed 15K gauss.

6.9	Class N, 200°C insulation systems shall be used throughout with a maximum temperature

rise of 115°C above an ambient of 40°C.

6.10	The transformer shall be designed for natural convection cooling.

6.11	Transverse Mode noise attenuation shall be 3 dB at 1000 hertz and 20 dB per decade to

50 dB with a resistive load.

7.0	Cabinet Construction

7.1	Cabinet shall be attractive, functional, NEMA type 1 general purpose indoor enclosure.

7.2	Cabinet shall be manufactured from heavy gauge steel.  Base sub-structure shall be adequate for fork lifting.

7.3	Dimensions shall be:  ________”W x _________”D x ________”H.

7.4	Powder-coat paint finish with proper pre-treatment shall be provided.

8.0	Warranty

The manufacturer shall guarantee all systems to be free from defects in material and workmanship for a period of (1) year following shipment from the factory.