CONTROLLED POWER COMPANY

GUIDE SPECIFICATION

FOR THE POWER COMMANDER

SERIES 900 ELECTRONIC LINE VOLTAGE REGULATOR

1.0	General

This specification describes the electrical and physical aspects of an electronic line voltage regulator (EVR). All systems shall be designed and manufactured to assure maximum reliability, flexibility, serviceability and performance.  The EVR shall use seamless electronic control to provide output voltage regulation within 1% of nominal within the correction time specified. The output shall be adjustable + 10% from nominal with an internal potentiometer.

The system shall be Controlled Power Company’s Power Commander Series 900 or Owner / Engineer approved Equal.

2.0	Standards

The EVR shall be designed in accordance with applicable portions of the following standards:

- Institute of Electrical and Electronic Engineers (IEEE 597)

- National Fire Protection Association (NFPA) 70, National Electrical Code (NEC)

- Underwriters Laboratory (UL 1012)

3.0	Performance Specifications

3.1	System Rating:  The system shall be rated at ______________ KVA.

3.2	Input Voltage - Nominal A.C. input voltage shall be ____________ Volts, _____ Phase.

3.3	Output Voltage - Nominal A.C. output voltage shall be ____________Volts, _____ Phase.

3.4	Output Voltage Regulation - Shall be + 1% or better for input voltage fluctuations of +10% to

-20% of nominal, and from no load to full load.

3.5	Remote Sensing - The output voltage shall be able to be sensed and regulated at the load, automatically compensating for line and wire losses due to long distances to the load.

3.6	Frequency Range - Shall be 57 to 63 Hz for 60 Hertz models, or 48 to 52 Hz for 50 Hertz models.

3.7	Output Voltage Adjustment Range - Shall be adjustable to + 10% with internally located potentiometer.

3.8	Correction Time - Shall be 5 to 9 cycles under worst case conditions.

3.9	Efficiency - Shall be 91% to 94%, KVA size dependent.

3.10	Power Factor - Shall be 0.95 typical at full load.

3.11	Harmonic Content - Less than 5% THD shall be added under linear load.

3.12	Overload Capability - Shall be 500% for 10 seconds, 1000% for one cycle.  Shall conform to IEEE 597.

3.13	Audible Noise - Shall be less than 60dBA @ 1 meter.

4.0	Regulating Transformer

4.1	Transformers shall be buck-boost dry type, convection or fan air cooled, 600 volt class.

4.2	The transformer shall be electrically and magnetically regulated with no moving parts.

4.3	All transformer windings shall be class N (200 C) insulated copper.

4.4	A class N installation system shall be utilized throughout with operating temperatures not to exceed 115C over a 40C ambient temperature.

4.5	Transformer core manufactured shall utilize M-6 grade, grain oriented, stress relieved silicon transformer steel.

4.6	Interface terminals shall be provided for input and output conductors.

4.7	All leads, wires and terminals shall be labeled to correspond with circuit wiring diagram.

4.8	Transformers shall be vacuum impregnated with an epoxy resin.

5.0	Cabinet Construction

5.1	Cabinet shall be attractive, functional, NEMA type 1 general purpose indoor enclosure.

5.2	Cabinet shall be manufactured from heavy gauge steel.  Base sub-structure shall be adequate for fork lifting.

5.3	Dimensions shall be:  ________”W x _________”D x ________”H.

5.4	Powder-coat paint finish with proper pre-treatment shall be provided.

6.0	Warranty

The manufacturer shall guarantee all systems to be free from defects in material and workmanship for a period of (1) year following shipment from the factory.