eLITE Model ELN Centralized Emergency Lighting Inverter

Guide Specification for 550 Watt – 1.5 KW Systems

- Part 1

- 1.0	General

This specification defines the electrical and mechanical characteristics and requirements for an uninterruptible stored emergency power supply system. The system as specified herein includes all the components required to deliver reliable, high quality uninterruptible power for emergency illumination and related life safety equipment. The system shall be designed for PFC electronic driver and/or ballast loading up to 50% of the rated output, and other lighting loads up to 100% of the rated output. The system consists of a microprocessor controlled transistorized PWM inverter, high speed transfer devices, constant voltage regulating transformer, battery charging system, energy storage battery platform, a diagnostic monitoring display panel, and all the related hardware components and software to facilitate a functional centralized system. The emergency power supply system shall provide immunity from all line disturbances and power interruptions. The system includes an uninterrupted, normally on output power section and a normally off standby output power section, thus enabling compatibility with emergency lighting fixtures operating in normally on mode and a standby operating mode. A self-diagnostic monitoring alarm system continuously advises of system status and battery condition.

- 1.1	Standards

The system shall be designed in accordance with applicable portions of the following standards:

- American National Standards Institute (ANSI C57.110).

- Institute of Electrical and Electronic Engineers (IEEE 519-1992) (C62.41-1991).

- National Electrical Manufacturers Association (NEMA PE-1).

- National Electric Code (NEC 2005) (NEC 2005, Article 700).

- National Fire Protection Association (NFPA 70) (NFPA 101).

- Underwriters Laboratories (UL 924).

- Federal Communications Commission (FCC Part 15, Sec. J, Class A).

- Federal Aviation Administration (FAA-G-201e).

- Listed UL Standards UL 924 Emergency Lighting Equipment with 90 minutes, (or UL 924 Auxiliary Lighting and Power Equipment for other than 90 minutes battery back up time), UL 1778 UPS Equipment, and C-UL listing to CSA C22.2, No. 107.1-M01 Canadian Standards for UPS Equipment.

- 1.2	Submittals

    - The manufacturer shall supply documentation for the installation of the system, including wiring diagrams and cabinet outlines showing dimensions, weights, BTUs, input/output current, input/output connection locations and required clearances.

    - The manufacturer shall be ISO9001 “Quality Assurance Certified” and shall upon request furnish certification documents.

    - The manufacturer shall be a United States based manufacturer with 5 years experience or greater in design and fabrication of centralized stored electrical energy emergency and standby power systems.

    - Factory test results shall be provided to show compliance with the requirements. The manufacturer shall include battery test documentation to validate the specified minimum emergency reserve with full rated KW load.

    - The supplier shall furnish (6) equipment submittal copies. Submittals shall be specific for the equipment furnished and shall include as-built information.

Part 2

- 2.1	Manufacturers

The equipment specified shall be the eLITE  Model ELN  centralized emergency lighting inverter system, manufactured by Controlled Power Company.

2.2        Manufactured Units

The system shall be designed and manufactured to assure maximum reliability, serviceability and performance. The system’s microprocessor, transistorized PWM inverter, highly filtered current and voltage regulated 2 stage battery charger, and high speed transfer devices shall be provided as one single main PC board for rapid service or replacement. The main PC board, constant voltage regulating transformer and filtering components shall be installed into one single main control module for rapid module service or replacement. The diagnostic monitor panel display and display select push button shall be mounted on the front of the system for easy operation and viewing. The system is to be furnished with an internally located AC input circuit breaker and AC output circuit breakers. The battery and DC conductors shall be DC fuse protected. All conductors and transformer windings shall be copper constructed. Cabinets are wall and/or floor mountable, constructed of  steel, front accessible through a hinged, key lockable door and shall be NEMA 2 drip proof rated for indoor use. Cabinet dimensions shall not exceed 31” W x 16.6”D x 39”H.

    - System shall operate in accordance with requirements as specified herein to support PFC electronic ballast loading up to 50% of the rated output, and other lighting loads up to 100% of the rated output. “Normally on” and “Normally off” AC output bus shall be 100% rated and limited only by the system maximum KW output rating.

    - Normal Operation: The load is supplied with voltage regulated and isolated power derived from the output regulating transformer. When utility AC power is present, the battery charger maintains a ripple free float charge on the batteries.

    - Uninterrupted Emergency Operation: Upon the failure or unacceptable deviation of commercial AC power, battery power is converted by the PWM inverter and filtered through the on-line regulating output transformer. There shall be no break or interruption of power to the load upon failure or restoration of the commercial AC power. Any transfer time resulting in a break or loss of power is unacceptable with reference to the uninterrupted output.

    - Standby Emergency Operation: Upon the failure or unacceptable deviation of commercial AC power or upon a remote input “zone command on signal”, the standby,  normally off AC output section of the system shall become energized, thus providing emergency power for standby lighting fixtures which are required to illuminate only in the event of emergency. Field adjustable timers shall be be included for use with on and off delay transition requirements.

    - Automatic Restart: In the case of a commercial power outage that exceeds the battery run time requirement, the output of the inverter shall shut off, but automatically restart once commercial AC power returns. Recharging of the batteries shall commence immediately.

    - System Power Output Capability: The stored emergency power supply system output power rating shall be (1500 watts) (1000 watts) (550 watts).

    - Battery Time Reserve Capacity: Battery shall be capable of producing emergency power for  (90) minutes at full rated Watts.

    - Reliability: MTBF 100,000 hours. MTTR, 1 Hour.

Part 3

3.1	Input Specifications

- Input Voltage: 120 VAC or 277 VAC.

- Input Voltage Operating Range:  +10% to -15% at full load without battery usage.

- Extended Range: The unit shall incorporate the use of variable range logic in conjunction with the load percentage to extend the input range up to +10% to -40% without battery usage while maintaining a regulated, usable output voltage.

- Frequency Range:  57.5 Hz to 62.5 Hz.

- Power Factor:  Self correcting to >0.95 (approaching unity).

- Input Harmonics:  < 5% THD (total harmonic distortion).

- Spike Attenuation:  3000:1.

3.2	Output Specifications

- Output Voltage: 120 VAC or 277 VAC.

- Sine Wave Voltage:  Maximum 5% harmonic distortion under linear load.

- Crest Factor:  3.0 : 1.

- Harmonic Attenuation:  Reflected load generated harmonics shall be attenuated 23dB at the input.

- Line Voltage Regulation: +/-3%.

- Load Regulation:  Typically better than +/-3%.

- Output Power Rating: KVA at 1.0 power factor (unity). KVA = KW

- Isolation:  NEC article 250-5d, shall comply with this standard that specifies a separately derived power source.

3.3	Battery Specifications

- Battery Time: 90 Minutes at full rated kilowatt output capability, UL 924 Emergency Lighting Equipment listed. (__) Minutes at full rated kilowatt output capability, UL924 Auxiliary Lighting and Power Equipment listed. (__) Minutes at full rated kilowatt output capability, C-UL listing to CSA C22.2, No. 107.1-M01 Canadian Standards for UPS Equipment.

- Battery Type:  Integral, valve regulated, sealed lead calcium, maintenance free.

- Charger:  3 Amp, full wave, two stage, filtered.

- Recharge Time:  UL 924, NFPA 101 compliant.

- Bus Voltage:  24 VDC, Float 2.27 VPC, final 1.75 VPC.

3.4	Performance Specifications

    - Overload Capability:  125% for ten minutes.

    - Surge Capability:  150% of rated output without need of static bypass.

    - Frequency Stability:  +0.2 Hz.

    - Inner Winding Capacitance:  0.01 pF (primary to secondary coupling).

    - Common Mode:  120 dB (106 : 1 ground noise attenuation).

    - Transverse Mode:  70 dB (3160 : 1 line noise attenuation).

    - Reactive Power Correction:  Load at .6 pf corrected to > 0.95 at input (automatically correcting).

    - Efficiency: 89% typical under full rated load.

    - Reliability: 100,000 hours MTBF.

    - Loading Profile: Designed for PFC electronic driver and/or ballast loading up to 50% of the rated output, and other lighting loads up to 100% of the rated output.

3.5	Environmental Specifications

- Operating Temperature:  0°C (32°F) to 40°C (105°F).

- Storage Temperature:  -20°C to 50°C.

- Relative Humidity:  95% non-condensing.

- Elevation:  5,000 feet, 1,500 meters.

- Weight and Inverter Cabinet Sizes:

Wattage Rating		Weight 		Dimensions W x D x H

550			344 lbs.		31” x 16.6” x 39”

1000			426 lbs.		31” x 16.6” x 39”

- 510 lbs.		31” x 16.6” x 39”

- Audible Noise Level: Not greater than 50 dba.

- Enclosure: NEMA 2. Drip proof for indoor use. Sealed, prohibiting rodent entry.

Part 4

4.1	 Display Monitor and Diagnostics

    - Display Panel –  System shall include a local, front mounted, sealed, alphanumeric LED display. Display shall indicate inverter input voltage, inverter output voltage, % load, and % battery as selected using a display select push button. System display panel shall include automatic visual status indicators for system on, system on battery, low battery and general alarm. Include audible alarm for system on battery, low battery and general alarm condition(s).

    - Communications Port (RS232) – Include communications port for remote monitoring access to general alarm conditions and electrical measurements.

    - General Alarm Conditions – Shall include: Loss of AC input power, low battery warning, frequency fault, check battery, shorted SCR, low battery shutdown, low output voltage, high output voltage, system overload and system over temperature warning.

    - Electrical Measurements – Shall include: AC input voltage, AC output voltage, output amps, % load, % battery voltage, output watts, output va, power factor, input line frequency, number of power outages recorded from last clear function, and number of overloads recorded from last clear function.

4.2	Relay Communications Interface

Status / Alarm open collector transistor interface shall be provided for use with optional remote annunciator panel or automatic message dialer. Inverter on, utility AC power failure (system using battery power), low battery  warning, and general alarm signals shall be included.

Part 5

5.1	Accessories (Optional Equipment)

    - Include automatic message dialer for telephone messaging to inform maintenance personnel of system alarm conditions for system on emergency battery power, low battery warning and general alarm.

    - Include remote annunciator panel for remote status indication of system alarm conditions for system on emergency battery power, low battery warning, and general alarm. The annunciator panel shall be provided with an interface cable of (50) (100) (150) (200) feet to connect to the inverter communication port.

    - Include (Quantity) control device(s) (dimmer control, wall switch, occupancy sensor) override for use with normally on inverter output bus to provide full illumination to designated emergency lights upon the failure or loss of commercial AC power.

    - Include (Quantity) zone sensing device(s) to sense voltage at individual zone lighting panels. The sensing device shall detect loss of power at the panel and shall signal the system to illuminate emergency fixtures within the specific zone only. If commercial AC power is acceptable at other zones, emergency lighting shall remain in the standby mode.

    - Include (3 output circuit breakers) (1 monitored output circuit breaker) on 550 watt rated unit’s normally off output bus.

Include (6 output circuit breakers) (3 monitored output circuit breakers) on (1000) (1500) watt rated unit’s normally off output bus.

    - Include system output circuit breaker open or tripped alarm contacts on all output circuit breakers for use with remote and/or local annunciation indicators.

    - Include network device SNMP / Ethernet  TCP/IP adapter for network communication of inverter system status and electrical measurement data.

    - Include network device SNMP / MODBUS TCP / Ethernet  TCP/IP adapter for network communication of inverter system status and electrical measurement data.

    - Include network device SNMP / MODBUS TCP & RS485 / Ethernet  TCP/IP adapter for network communication of inverter system status and electrical measurement data.

Part 6

6.1	Warranty

    - The manufacturer shall guarantee all power components and system electronics to be free from defects in material and workmanship for a period of 2 years following shipment from the factory.

    - Battery warranty shall be 1 year full replacement, 14 years pro-rated.

6.2	Serviceability

The system shall be constructed of one front-accessible electronics module subassembly. The electronics module shall include AC terminals and a DC Anderson connector for rapid replacement. Batteries shall be positioned and wired to facilitate rapid replacement.